## Blank Template
Category | TIA-1179-B Requirement | Current / Proposed Condition | Compliance Status | Action Needed
Horizontal Cabling | All new horizontal cabling shall be minimum Category 6A, including patch cords and connectors, per TIA-568. Supports 10 Gb/s applications.
Backbone Cabling | Backbone cabling shall include both OM4 multimode and OS2 single-mode optical fiber.
Telecommunications Rooms | Dedicated telecommunications rooms are required on each floor, designed per TIA-569-D. TRs must include proper grounding, cooling, security, and space for future growth.
Port Density | TIA-1179-B specifies functional area outlet densities: e.g., 2-6 per work area in administrative zones, higher in imaging, surgery, and critical care spaces.
Grounding & Bonding | Telecommunications Grounding Busbar required in each TR, bonded per ANSI/TIA-607 and NEC.
Labeling & Documentation | All cabling, pathways, and spaces must be labeled and documented per TIA-606-D, including complete as-built documentation.
Security & Access Control | Access to telecom spaces must be restricted to authorized personnel, with controls per TIA-5017 and HIPAA requirements.
Pathways & Spaces | Pathways and spaces must comply with TIA-569-D. Spare capacity required for growth and maintenance access.
Redundancy & Resiliency | Diverse backbone pathways and dual entrance facilities are recommended for resiliency in critical healthcare environments.
Wireless Support | Design must support high-density wireless access points (WAPs) with sufficient cabling and pathways.
Specialty Areas (Clinical) | Clinical spaces such as imaging, surgery, and critical care must include higher port densities to support specialized medical devices and IT systems.
Power & UPS | TRs must include dedicated electrical circuits and are strongly recommended to have UPS to maintain continuity of telecom equipment.

## Example
Category | TIA-1179-B Requirement | Current / Proposed Condition | Compliance Status | Action Needed
Horizontal Cabling | All new horizontal cabling shall be minimum Category 6A, including patch cords and connectors, per TIA-568. Supports 10 Gb/s applications. | Mix of non-category, Cat 3, Cat 5 cabling. Not compliant. Recommendation: replace with Cat 6A across campus | Not Compliant | Replace all horizontal cabling with Cat 6A channels incl. patch cords, panels, jacks
Backbone Cabling | Backbone cabling shall include both OM4 multimode and OS2 single-mode optical fiber. | Antiquated twisted pair and OM1 fiber backbones. Lacks compliance. Recommendation: replace with OS2 SM + OM4 MM fiber | Not Compliant | Demolish OM1 fiber/copper backbone, install OS2 SM + OM4 MM with 12 strands each
Telecommunications Rooms | Dedicated telecommunications rooms are required on each floor, designed per TIA-569-D. TRs must include proper grounding, cooling, security, and space for future growth. | Many TRs undersized, shared with electrical, no cooling, no access control. Recommendation: build dedicated TRs with HVAC, security, grounding | Not Compliant | Construct dedicated TRs per floor with grounding, HVAC, access control
Port Density | TIA-1179-B specifies functional area outlet densities: e.g., 2-6 per work area in administrative zones, higher in imaging, surgery, and critical care spaces. | Existing patient/office spaces below TIA-1179 outlet density. Recommendation: Add Cat 6A outlets per functional area | Partially Compliant | Increase outlet counts in patient rooms, nurse stations, imaging per TIA-1179 density
Grounding & Bonding | Telecommunications Grounding Busbar required in each TR, bonded per ANSI/TIA-607 and NEC. | Grounding busbars present in all TRs | Compliant | No action needed
Labeling & Documentation | All cabling, pathways, and spaces must be labeled and documented per TIA-606-D, including complete as-built documentation. | Labeling inconsistent or absent. Recommendation: relabel all cabling per TIA-606 | Not Compliant | Relabel all cables and outlets per TIA-606
Security & Access Control | Access to telecom spaces must be restricted to authorized personnel, with controls per TIA-5017 and HIPAA requirements. | TRs currently use standard building keys shared with maintenance staff. No access logging. | Not Compliant | Install electronic card access with audit trail; restrict access to IT staff only.
Pathways & Spaces | Pathways and spaces must comply with TIA-569-D. Spare capacity required for growth and maintenance access. | Existing conduits at 80% fill; some tray routing shares pathways with electrical conduits. | Partially Compliant | Add dedicated cable tray for telecom cabling; ensure minimum 40% spare capacity.
Redundancy & Resiliency | Diverse backbone pathways and dual entrance facilities are recommended for resiliency in critical healthcare environments. | Facility currently has a single entrance room and no diverse backbone paths. | Not Compliant | Design secondary entrance facility; provide alternate riser path for redundancy.
Wireless Support | Design must support high-density wireless access points (WAPs) with sufficient cabling and pathways. | Some APs installed with Cat 5e cabling; density is below healthcare recommendation. | Partially Compliant | Upgrade AP cabling to Cat 6A; increase WAP density in clinical and waiting areas.
Specialty Areas (Clinical) | Clinical spaces such as imaging, surgery, and critical care must include higher port densities to support specialized medical devices and IT systems. | Imaging rooms have minimal outlets; no redundant fiber backbone connections provisioned. | Not Compliant | Add fiber backbone redundancy; increase outlet density in ORs, imaging, and labs per TIA-1179-B.
Power & UPS | TRs must include dedicated electrical circuits and are strongly recommended to have UPS to maintain continuity of telecom equipment. | TRs connected to building power only; no UPS present. | Not Compliant | Install dedicated circuits with UPS to support telecom racks and active equipment.