## FLUSH CVR DUCT-D,F,G,FS
Wiring Duct Size Selector: Types D, F, G & FS |  |  |  |  | Suitable Duct Sizes at 50% wire fill
See Wiring Duct Selection Guide for additional information
1.) Determine Wire O.D. of Multiple Cables (Enter Wire Information) |  |  |  |  | Nominal Duct Size |  | Area
Wire | Number | O.D. |  |  | W | H |  | Size
1 | 10 | 1 | 10 |  | 0.5 | 0.5 | 0.25 | TOO SMALL
2 |  |  | 0 |  | 0.5 | 1 | 0.5 | TOO SMALL
3 |  |  | 0 |  | 0.5 | 2 | 1 | TOO SMALL
4 |  |  | 0 |  | 0.5 | 4 | 2 | TOO SMALL
5 |  |  | 0 |  | 0.75 | 0.75 | 0.5625 | TOO SMALL
6 |  |  | 0 |  | 0.75 | 1 | 0.75 | TOO SMALL
7 |  |  | 0 |  | 0.75 | 1.5 | 1.125 | TOO SMALL
8 |  |  | 0 |  | 0.75 | 2 | 1.5 | TOO SMALL
9 |  |  | 0 |  | 1 | 1 | 1 | TOO SMALL
10 |  |  | 0 |  | 1 | 1.5 | 1.5 | TOO SMALL
[5 empty] | 1 | 2 | 2 | TOO SMALL
2.) Multiple Wire O.D. Calculation |  |  |  |  | 1 | 3 | 3 | TOO SMALL
A.) Sum of #Wires x Wire O.D. |  |  | 10 |  | 1 | 4 | 4 | TOO SMALL
B.) Total Number of Wires |  |  | 10 |  | 1.5 | 1 | 1.5 | TOO SMALL
C.) Wire O.D. = A divided by B = |  |  | 1 |  | 1.5 | 1.5 | 2.25 | TOO SMALL
[5 empty] | 1.5 | 2 | 3 | TOO SMALL
3.) Wire Area Calculation |  |  |  |  | 1.5 | 3 | 4.5 | TOO SMALL
Wire Area= πr² x B (total # of wires) |  |  | 7.854 | in2 | 1.5 | 4 | 6 | TOO SMALL
D.) Comparison Area to maintain a 50% wire fill in profile* |  |  |  |  | 2 | 1 | 2 | TOO SMALL
= B x (1.75 x (C squared)) |  |  | 17.5 | in2 | 2 | 1.5 | 3 | TOO SMALL
[5 empty] | 2 | 2 | 4 | TOO SMALL
4.) Pick a size large enough for the Wire Area |  |  |  |  | 2 | 3 | 6 | TOO SMALL
E.) See table at right, check to confirm size is available in the Duct Type needed. |  |  |  |  | 2 | 4 | 8 | TOO SMALL
[5 empty] | 2 | 5 | 10 | TOO SMALL
[5 empty] | 2.5 | 3 | 7.5 | TOO SMALL
Wirefill Calculator (Enter Selected Duct Size to Confirm Wirefill) |  |  |  |  | 3 | 1 | 3 | TOO SMALL
1. Enter Duct Size Selected |  |  |  |  | 3 | 2 | 6 | TOO SMALL
A.) Duct Width |  |  | 2 |  | 3 | 3 | 9 | TOO SMALL
B.) Duct Height |  |  | 3 |  | 3 | 4 | 12 | TOO SMALL
C.) Wire O.D. |  |  | 1 |  | 3 | 5 | 15 | TOO SMALL
[5 empty] | 4 | 1.5 | 6 | TOO SMALL
2. Wirefill Calculation |  |  |  |  | 4 | 2 | 8 | TOO SMALL
D.) A x B divided by 1.75 x (C squared) |  |  | 3 | wires at 50% fill | 4 | 3 | 12 | TOO SMALL
[5 empty] | 4 | 4 | 16 | TOO SMALL
3.) Is duct size selected large enough at 50% fill? |  |  | NO |  | 4 | 5 | 20 | OK
[5 empty] | 6 | 4 | 24 | OK
*Comparison Area accounts for some air space between wires and design features extending inside the duct profile. In actual practice a 50% wirefill is the maximum amount of wiring the duct can hold;
A 50% max wire fill is specified by NFPA79-2007, sec 13.5.2
Note: To the best of our knowledge the above information is accurate. PANDUIT® assumes no liability for the accuracy or completeness of this information. | [7 empty] | Revised 2/1/2024
This file is the property of Panduit Corporation.

## METRIC DUCT-MC,NNC,TMC
Wiring Duct Size Selector: Type MC, NNC, TMC Metric Wiring Duct | [5 empty] | Suitable Duct Sizes at 50% wire fill
See Wiring Duct Selection Guide for additional information
1.) Determine Wire O.D. of Multiple Cables (Enter Wire Information) | [5 empty] | Nominal Duct Size |  | Area
Wire | Number | O.D. (inches) | (mm) | (mm) |  | W (mm) | H (mm) |  | Size
1 | 10 | 1 | 25.4 | 254 |  | 25 | 25 | 625 | TOO SMALL
2 |  |  | 0 | 0 |  | 25 | 37 | 925 | TOO SMALL
3 |  |  | 0 | 0 |  | 25 | 50 | 1250 | TOO SMALL
4 |  |  | 0 | 0 |  | 25 | 62 | 1550 | TOO SMALL
5 |  |  | 0 | 0 |  | 25 | 75 | 1875 | TOO SMALL
6 |  |  | 0 | 0 |  | 37 | 37 | 1369 | TOO SMALL
7 |  |  | 0 | 0 |  | 37 | 50 | 1850 | TOO SMALL
8 |  |  | 0 | 0 |  | 37 | 62 | 2294 | TOO SMALL
9 |  |  | 0 | 0 |  | 37 | 75 | 2775 | TOO SMALL
10 |  |  | 0 | 0 |  | 50 | 50 | 2500 | TOO SMALL
[6 empty] | 50 | 75 | 3750 | TOO SMALL
2.) Multiple Wire O.D. Calculation | [5 empty] | 50 | 100 | 5000 | TOO SMALL
A.) Sum of #Wires x Wire O.D. |  |  |  | 254 |  | 62 | 37 | 2294 | TOO SMALL
B.) Total Number of Wires |  |  |  | 10 |  | 62 | 62 | 3844 | TOO SMALL
C.) Wire O.D. = A divided by B = |  |  |  | 25.4 |  | 75 | 50 | 3750 | TOO SMALL
[6 empty] | 75 | 62 | 4650 | TOO SMALL
3.) Wire Area Calculation | [5 empty] | 75 | 75 | 5625 | TOO SMALL
Wire Area= πr² x B (total # of wires) |  |  |  | 5067.0748 | mm² | 75 | 100 | 7500 | TOO SMALL
D.) Comparison Area to maintain a 50% wire fill in profile* | [5 empty] | 100 | 50 | 5000 | TOO SMALL
= B x (1.75 x (C squared)) |  |  |  | 11290.3 | mm² | 100 | 62 | 6200 | TOO SMALL
4.) Pick a size large enough for the Wire Area | [5 empty] | 100 | 75 | 7500 | TOO SMALL
E.) See table at right, check to confirm size is available in the Duct Type needed. | [5 empty] | 100 | 100 | 10000 | TOO SMALL
Wirefill Calculator (Enter Selected Duct Size to Confirm Wirefill)
1. Enter Duct Size Selected
A.) Duct Width |  |  |  | 50 | mm
B.) Duct Height |  |  |  | 100 | mm
C.) Wire O.D. |  |  |  | 25.4
2. Wirefill Calculation
D.) A x B divided by 1.75 x (C squared) |  |  |  | 4 | wires at 50% fill
3.) Is duct size selected large enough at 50% fill? |  |  |  | NO
*Comparison Area accounts for some air space between wires and design features extending inside the duct profile. In actual practice a 50% wirefill is the maximum amount of wiring the duct can hold;
A 50% max wire fill is specified by NFPA79-2007, sec 13.5.2
Note: To the best of our knowledge the above information is accurate. PANDUIT® assumes no liability for the accuracy or completeness of this information. | [8 empty] | Revised 2/1/2024
This file is the property of Panduit Corporation.

## TRAD DUCT-NE,NS,PE,PS
Wiring Duct Size Selector: Type NE, NS |  |  |  |  | Suitable Duct Sizes at 50% wire fill
See Panduit catalog for available sizes by duct type
1.) Determine Wire O.D. of Multiple Cables (Enter Wire Information) |  |  |  |  | Nominal Duct Size |  | Area
Wire | Number | O.D. |  |  | W | H |  | Size
1 | 10 | 1 | 10 |  | 0.5 | 0.5 | 0.25 | TOO SMALL
2 |  |  | 0 |  | 0.5 | 1 | 0.5 | TOO SMALL
3 |  |  | 0 |  | 0.75 | 1 | 0.75 | TOO SMALL
4 |  |  | 0 |  | 1 | 1 | 1 | TOO SMALL
5 |  |  | 0 |  | 1 | 1.5 | 1.5 | TOO SMALL
6 |  |  | 0 |  | 1 | 2 | 2 | TOO SMALL
7 |  |  | 0 |  | 1 | 3 | 3 | TOO SMALL
8 |  |  | 0 |  | 1 | 4 | 4 | TOO SMALL
9 |  |  | 0 |  | 1.5 | 1.5 | 2.25 | TOO SMALL
10 |  |  | 0 |  | 1.5 | 2 | 3 | TOO SMALL
[5 empty] | 1.5 | 3 | 4.5 | TOO SMALL
2.) Multiple Wire O.D. Calculation |  |  |  |  | 1.5 | 4 | 6 | TOO SMALL
A.) Sum of #Wires x Wire O.D. |  |  | 10 |  | 2 | 1 | 2 | TOO SMALL
B.) Total Number of Wires |  |  | 10 |  | 2 | 1.5 | 3 | TOO SMALL
C.) Wire O.D. = A divided by B = |  |  | 1 |  | 2 | 2 | 4 | TOO SMALL
[5 empty] | 2 | 3 | 6 | TOO SMALL
[5 empty] | 2 | 4 | 8 | TOO SMALL
3.) Wire Area Calculation |  |  |  |  | 3 | 1 | 3 | TOO SMALL
Wire Area= πr² x B (total # of wires) |  |  | 7.854 | in2 | 3 | 1.25 | 3.75 | TOO SMALL
D.) Comparison Area to maintain a 50% wire fill in profile* |  |  |  |  | 3 | 2 | 6 | TOO SMALL
= B x (2.00 x (C squared)) |  |  | 20 | in2 | 3 | 3 | 9 | TOO SMALL
[5 empty] | 3 | 4 | 12 | TOO SMALL
4.) Pick a size large enough for the Wire Area |  |  |  |  | 3 | 5 | 15 | TOO SMALL
E.) See table at right, check to confirm size is available in the Duct Type needed. |  |  |  |  | 4 | 2 | 8 | TOO SMALL
[5 empty] | 4 | 3 | 12 | TOO SMALL
Wirefill Calculator (Enter Selected Duct Size to Confirm Wirefill) |  |  |  |  | 4 | 4 | 16 | TOO SMALL
1. Enter Duct Size Selected |  |  |  |  | 4 | 5 | 20 | TOO SMALL
A.) Duct Width |  |  | 2
B.) Duct Height |  |  | 4
C.) Wire O.D. |  |  | 1
2. Wirefill Calculation
D.) A x B divided by 2.0 x (C squared) |  |  | 4 | wires at 50% fill
3.) Is duct size selected large enough at 50% fill? |  |  | NO
*Comparison Area accounts for some air space between wires and design features extending inside the duct profile. In actual practice a 50% wirefill is the maximum amount of wiring the duct can hold;
A 50% max wire fill is specified by NFPA79-2007, sec 13.5.2
Note: To the best of our knowledge the above information is accurate. PANDUIT® assumes no liability for the accuracy or completeness of this information. | [7 empty] | Revised 2/1/24
This file is the property of Panduit Corporation.

## HINGED CVR DUCT-H
Wiring Duct Size Selector: Type H, HN, HS Hinged Cover Duct |  |  |  |  | Suitable Duct Sizes at 50% wire fill
See Panduit catalog for available sizes by duct type
1.) Determine Wire O.D. of Multiple Cables (Enter Wire Information) |  |  |  |  | Nominal Duct Size |  | Area
Wire | Number | O.D. |  |  | W | H |  | Size
1 | 10 | 1 | 10 |  | 1.5 | 2 | 3 | TOO SMALL
2 |  |  | 0 |  | 1.5 | 3 | 4.5 | TOO SMALL
3 |  |  | 0 |  | 2 | 2 | 4 | TOO SMALL
4 |  |  | 0 |  | 2 | 3 | 6 | TOO SMALL
5 |  |  | 0 |  | 2 | 4 | 8 | TOO SMALL
6 |  |  | 0 |  | 3 | 3 | 9 | TOO SMALL
7 |  |  | 0 |  | 3 | 4 | 12 | TOO SMALL
8 |  |  | 0 |  | 4 | 4 | 16 | TOO SMALL
9 |  |  | 0
10 |  |  | 0
2.) Multiple Wire O.D. Calculation
A.) Sum of #Wires x Wire O.D. |  |  | 10
B.) Total Number of Wires |  |  | 10
C.) Wire O.D. = A divided by B = |  |  | 1
3.) Wire Area Calculation
Wire Area= πr² x B (total # of wires) |  |  | 7.854 | in2
D.) Comparison Area to maintain a 50% wire fill in profile*
= B x (1.85 x (C squared)) |  |  | 18.5 | in2
4.) Pick a size large enough for the Wire Area
E.) See table at right, check to confirm size is available in the Duct Type needed.
Wirefill Calculator (Enter Selected Duct Size to Confirm Wirefill)
1. Enter Duct Size Selected
A.) Duct Width |  |  | 2
B.) Duct Height |  |  | 4
C.) Wire O.D. |  |  | 1
2. Wirefill Calculation
D.) A x B divided by 1.85 x (C squared) |  |  | 4 | wires at 50% fill
3.) Is duct size selected large enough at 50% fill? |  |  | NO
*Comparison Area accounts for some air space between wires and design features extending inside the duct profile. In actual practice a 50% wirefill is the maximum amount of wiring the duct can hold;
A 50% max wire fill is specified by NFPA79-2007, sec 13.5.2
Note: To the best of our knowledge the above information is accurate. PANDUIT® assumes no liability for the accuracy or completeness of this information. | [7 empty] | Revised 2/1/24
This file is the property of Panduit Corporation.

## CORNER WIRING DUCT
Wiring Duct Size Selector: PANELMAX™ Corner Wiring Duct | [5 empty] | Suitable Duct Sizes at 50% wire fill
See Panduit catalog for available sizes by duct type
1.) Determine Wire O.D. of Multiple Cables (Enter Wire Information) | [5 empty] | Nominal Duct Size |  | Internal Area
Wire | Number | O.D. |  |  |  | W | H |  | Size
1 | 10 | 1 | 10 |  | CWD3 | 4.4 | 3.57 | 17.58 | TOO SMALL
2 |  |  | 0 |  | CWD4 | 5.33 | 4.58 | 26.92 | OK
3 |  |  | 0
4 |  |  | 0
5 |  |  | 0
6 |  |  | 0
7 |  |  | 0
8 |  |  | 0
9 |  |  | 0
10 |  |  | 0
2.) Multiple Wire O.D. Calculation
A.) Sum of #Wires x Wire O.D. |  |  | 10
B.) Total Number of Wires |  |  | 10
C.) Wire O.D. = A divided by B = |  |  | 1
3.) Wire Area Calculation
Wire Area= πr² x B (total # of wires) |  |  | 7.854 | in2
D.) Comparison Area to maintain a 50% wire fill in profile*
= B x (2.0 x (C squared)) |  |  | 20 | in2
4.) Pick a size large enough for the Wire Area
E.) See table at right, check to confirm size is available in the Duct Type needed.
Wirefill Calculator (Total Capacity at this wire OD)
1.) Corner Wiring Duct Capacity
|  | CWD3 | 8 | wires at 50% fill
|  | CWD4 | 13 | wires at 50% fill
*Comparison Area accounts for some air space between wires and design features extending inside the duct profile. In actual practice a 50% wirefill is the maximum amount of wiring the duct can hold;
A 50% max wire fill is specified by NFPA79-2007, sec 13.5.2
Note: To the best of our knowledge the above information is accurate. PANDUIT® assumes no liability for the accuracy or completeness of this information. | [8 empty] | Revised 2/1/24
This file is the property of Panduit Corporation.

## FLEXIBLE DUCT-FL
Wiring Duct Size Selector: Type FL Flexible Wiring Duct | [5 empty] | Suitable Duct Sizes at 50% wire fill
See Panduit catalog for available sizes by duct type
1.) Determine Wire O.D. of Multiple Cables (Enter Wire Information) | [5 empty] | Nominal Duct Size |  | Area
Wire | Number | O.D. (inches) | (mm) | (mm) |  | W (mm) | H (mm) |  | Size
1 | 10 | 1 | 25.4 | 254 |  | 12 | 12 | 144 | TOO SMALL
2 |  |  | 0 | 0 |  | 25 | 25 | 625 | TOO SMALL
3 |  |  | 0 | 0 |  | 50 | 50 | 2500 | TOO SMALL
4 |  |  | 0 | 0
5 |  |  | 0 | 0
6 |  |  | 0 | 0
7 |  |  | 0 | 0
8 |  |  | 0 | 0
9 |  |  | 0 | 0
10 |  |  | 0 | 0
2.) Multiple Wire O.D. Calculation
A.) Sum of #Wires x Wire O.D. |  |  |  | 254
B.) Total Number of Wires |  |  |  | 10
C.) Wire O.D. = A divided by B = |  |  |  | 25.4
3.) Wire Area Calculation
Wire Area= πr² x B (total # of wires) |  |  |  | 5067.0748 | mm²
D.) Comparison Area to maintain a 50% wire fill in profile*
= B x (2.5 x (C squared)) |  |  |  | 16129 | mm²
4.) Pick a size large enough for the Wire Area
E.) See table at right, check to confirm size is available in the Duct Type needed.
Wirefill Calculator (Enter Selected Duct Size to Confirm Wirefill)
1. Enter Duct Size Selected
A.) Duct Width |  |  |  | 12 | mm
B.) Duct Height |  |  |  | 12 | mm
C.) Wire O.D. |  |  |  | 25.4
2. Wirefill Calculation
D.) A x B divided by 1.75 x (C squared) |  |  |  | 0 | wires at 50% fill
3.) Is duct size selected large enough at 50% fill? |  |  |  | NO
*Comparison Area accounts for some air space between wires and design features extending inside the duct profile. In actual practice a 50% wirefill is the maximum amount of wiring the duct can hold;
A 50% max wire fill is specified by NFPA79-2007, sec 13.5.2
Note: To the best of our knowledge the above information is accurate. PANDUIT® assumes no liability for the accuracy or completeness of this information. | [8 empty] | Revised 2/1/24
This file is the property of Panduit Corporation.